April 3, 2023

The Benton Irrigation District’s (BID), Board of Directors (BOD) meeting was held at the District office on Highland Road in Benton City, WA beginning at 8 am

In Attendance: Chairman Robert Buoy, Director Tyler Wilson, Operations Manager Ed Mitchell, Office Manager Dianne Andrews.

Visitors: none

- Maintenance Report:

- Air conditioning Unit #2 at RPS broke in the same way that Unit #1 did last year.  There is a leak in the condenser coil that cannot be repaired due to it’s location.

- A replacement coil is 7-10 days out and would cost $7,900.  At that point, they would test the compressor.  If it’s bad, a new compresser is $7k+. There is also a possibility of using the smaller compressor off of Unit #1.

- The new unit for #1 is still on order and will currently be built in May, but that is not guaranteed.

- Currently we have 2 units working at 1/3 capacity and 1 portable unit.

- To ensure that we have sufficient cooling in the summer, the Board made the following motions:

Motion #1: To purchase an additional 20 ton unit to replace Unit #2 for approx. $30k

Motion #2: To order an additional 7 ton portable unit for backup for approx. $15k

Motion #3: To repair Unit #2’s coils and possibly compressor for approx. $8-16k

The motions were seconded and approved.

Director Tyler Wilson moved to adjourn the meeting, all in favor.

Meeting adjourned at 9 am.

Director    ___________________		Director    ___________________

Director    ___________________